## Instructions
Instructions:
Kitsap 911 strongly recommends using the spreadsheet to make it easier for the Proposer to meet Kitsap 911 requirements to provide a detailed list of equipment at the site for insurance purposes and the cost of equipment (including installation) per site. Furthermore, the spreadsheet format allows for identification of missing or duplicated parts. The system total and site totals allow for pricing cross checking for errors.
Complete both spreadsheets to comply with the RFP requirements. The first spreadsheet relates to the replacement of existing rectifiers and batteries. The second spreadsheet pertains to new sites being built by Kitsap 911.
Failure to submit the spreadsheets will likely result in a lower evaluation. The completed spreadsheet (Excel file) must be included in the sealed proposal package on a USB drive.
The Proposer is responsible for reviewing the Bill of Materials and Services spreadsheet and proposing any changes or corrections in the proposal submittal. Kitsap 911 is not responsible for any errors or omissions in the spreadsheet.
Spreadsheets Layout
Rows: The Bill of Materials and Services spreadsheets contain a unique row for each unique part number or service using the manufacturer’s description whenever possible.
Columns: The columns in the spreadsheet are split into two major groups. Columns A-G contain a unique item number, recommended source for parts if applicable, manufacturer’s part number, description, unit price, the total system quantity required, and the system price. The remaining columns, beginning with Column I, have each site listed in alphabetical order with the quantity of each unique part number for each site and the site subtotal for each line item. A "Spares" site is included at the end of the site columns. The New Site tab has applicable unique part numbers and only one site.
Using the Spreadsheets
1. Enter the unit price for each line item. The spreadsheet should automatically calculate the total system cost for the line item and the cost per site.
2. Do not enter the total quantities in column F. The quantities required are provided for each of the sites.
3. Similarly do not enter the cost for the line items per site i.e., columns J, L, N, etc. The site totals are calculated from the site quantities and the unit cost.
4. Wire costs are entered in cost per foot with site quantities in feet.
5. Blank rows are provided to allow the Proposer to introduce new materials or services.
6. To "remove" an existing line item from one or more sites, zero out the quantity from the site. Do not delete the row.
7. Services entries with hourly or daily rates are likely to result in higher evaluations.
8. Operations and Maintenance costs for years 1 through 7 must be provided. Failure to provide Operating and Maintenance Costs will prevent Kitsap 911 from calculating the total cost of ownership and is likely to result in a lower proposal evaluation.
Minimize Spreadsheet Changes
Kitsap 911 recommends minimal changes to the spreadsheets as modifications to the spreadsheets may impact the formulas in some cells.

## Replacement BOM&S
[7 empty] | CC |  | E30 |  | GM |  | HR |  | LH |  | MO |  | NH |  | OH |  | PU |  | SP |  | SU |  | TL |  | SPARES
| PRODUCT CODE |  | EQUIPMENT LIST | UNIT | SYSTEM |  | CENCOM |  | E30TH |  | GOLD MTN |  | HANSVILLE RD |  | LINCOLN HILL |  | MANDUS OLSON |  | NEWBERRY HILL |  | ORCHARD HGTS |  | PURDY |  | SIMON POINT |  | SUQUAMISH |  | TEAL LAKE
ITEM | PART NUMBER | SUPPLIER | DESCRIPTION | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE | QTY | PRICE
1 | RECTIFIER SYSTEMS
1.1 | Rectifer System
1.101 | UNT20806.00012 | ELTEK | UNITY POWER SYSTEM WITH FLATPACK2 - 48V, 500A POWER SHELF - RECTIFIER POSITIONS: QTY 8 (SUPPORTS BOTH 2000W and 3000W RECTIFIERS) - INPUT CONNECTIONS: REAR ACCESS TO TERMINAL BLOCK, ONE INPUT PER RECTIFIER, DUAL FEED JUMPERS INCLUDED PRIMARY DISTRIBUTION: 23" WIDE, NEGATIVE VOLTAGE OUTPUT QTY 26 CIRCUIT BREAKER POSITIONS (CBB STYLE) 1/4"-20 STUD 5/8" CENTER -QTY 26 LOAD BREAKER POSITIONS QTY 3 BULK LOAD POSITIONS -QTY 1: 3/8"-16 NUTS ON 1" CENTER -QTY 2: 1/4"-20 NUTS ON 5/8" CENTER BULK BATTERY POSITIONS THRU A SHUNT & LVBD -QTY 7: 3/8"-16 STUDS ON 1" CENTER OR QTY 8: 1/4"-20 NUTS ON 5/8" CENTER SMARTPACK S PANEL MOUNT CONTROLLER INCLUDED SPSP-UNT600-A01 UNT-F4808I-C14N |  | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
1.102 | D07 | ELTEK | DISTRIBUTION PANEL, SINGLE BUS FOR STANDALONE APPLICATIONS OR ADD TO EXISTING UNITY PLANT 23" WIDE MOUNTING 4RU REAR WIRE INPUT, FRONT WIRE OUPUT, 15" DEEP, MID MOUNT INPUT VOLTAGE: +/- 12/24/48VDC 600AMP BUS RATING QTY 4 INPUT CONNECTIONS 1/4'' ON 5/8'' CENTER AND QTY 1 INPUT CONNECTION 3/8" ON 1" CENTER QTY 26 BULLET CIRCUIT BREAKER POSITIONS, 1/4''-20 STUDS WITH 5/8'' CENTERS MAX CIRCUIT BREAKER SIZE 250AMPS DRY CONTACT ALARM, (2 PIN CONNECTOR WIRESET INCLUDED) (USING CBB BREAKERS ONLY) |  | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
1.103 | M2S22022.00041 | ELTEK | FP2-MPS2-15U-48V-A4-S3-D5-D9-B-C01 -48VDC MODULAR II POWER SYSTEM WITH 1,200A CAPACITY, INCLUDES: - RACK MOUNT 23", 22.26" DEEP, 22RU HIGH - CONTROLLER KIT: BASIC INDUSTRIAL MODULE, I/O MONITOR2 - QTY 6 INPUTS AND 6 OUTPUTS // QTY 3 TEMPERATURE PROBE INPUTS // QTY 3 FORM C RELAYS - QTY 3 BULK OUTPUTS POS & NEG TO SUPPORT THREE 750MCM CABLE FP2 3KW RECTIFIER BASE, THREE PHASE 208VAC (3W+PE), 3 RECTIFIERS PER AC INPUT, TERMINAL BLOCK (SINGLE HOLE LUG CONNECTION) INCLUDES: - QTY 5 FP2 3KW RECTIFIER SHELVES - EACH RECTIFIER SHELF HAS 4 RECTIFIER POSITIONS, TOTAL 20 RECTIFIER POSITIONS - THREE PHASE 208VAC (3W+PE) - QTY 3 RECTIFIERS PER AC INPUT (32.9A MAX AC INPUT PER FEED), TOTAL QTY 7 AC INPUTS - FRONT ACCESS, QTY 1 AC PANEL, EACH AC LANDING CONSISTS OF SINGLE HOLE #10-32" STUD, AND ACCEPTS MAX. LUG TONGUE WIDTH 0.47", MAX 6AWG WIRE - QTY 6 KNOCKOUTS FOR 1" CONDUIT ON THE TOP OF AC PANEL, QTY 5 SETS OF GROUNDING STUDS (1/4" ON 5/8") 1,200A BATTERY BULK OUTPUT PANEL, TOP REAR ACCESS, WITH LVBD INCLUDES: - REAR ACCESS CONNECTIONS - 1,200A LOW VOLTAGE BATTERY DISCONNECT (LVBD) - 50mV/,2000A SHUNT // BULK HOT AND RETURN BUS BARS - QTY 13 - 3/8" ON 1" CENTER BATTERY LANDINGS ON HOT AND RETURN BUS INCLUDING: - NEGATIVE AND POSITIVE BULK BUS SYSTEM CONNECTION - QTY 3 CONNECTION POINTS - 3/8" ON 1", MAX LUG TONGUE WIDTH OF 2.25" PER CONNECTION WATERFALL #1 LOAD DISTRIBUTION: - QTY 2 600A BULLET TPS/CBB BREAKER PANEL; 1/4" HOLE ON 5/8" CENTER; MAX LUG 5/8" WATERFALL #2 LOAD DISTRIBUTION: - QTY 1 600A BULLET TPS/CBB BREAKER PANEL; 1/4" HOLE ON 5/8" CENTER; MAX LUG 5/8" MODULAR II SMARTPACK2 TOUCH WITH -48V 1,200A STANDARD PROFILE - 4.4” GRAPHICAL HIGH RESOLUTION COLOR CAPACITIVE TOUCH DISPLAY - DUAL USB PORTS FOR DONGLES AND FLASH DRIVES - SERIAL PORT (RS232/RS485) FOR MODBUS RTU COMMUNICATION TO 3RD PARTY EQUIP. - DUAL ETHERNET PORTS (LAN AND DIRECT CONNECTION) - HTTPS/RADIUS/SNMP/MODBUS TCP/SNTP/SMTP/FTPS/IPV4/IPV6 - EVENT & DATA LOGGING/BATTERY DISCHARGE TEST/TEMPERATURE COMPENSATION - CAN POWER REQUIREMENTS: 180 MILLIAMPS |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1.104 | SP2TI-MP212-A01-VV | ELTEK | SMARTPACK2 TOUCH CONTROLLER UPGRADE/REPLACEMENT FOR MODULAR 2 SYSTEMS STANDARD CONFIGURATION FOR 48V,1200A SYSTEM POWERED BY CAN BUS (180 MILLIAMP) INCLUDES 4.4" GRAPHICAL HIGH RESOLUTION COLOR TOUCH DISPLAY, TWO ETHERNET PORTS , TWO USB PORTS, RS232/RS485 SERIAL PORT |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1.105 | 24100.601.VC | ELTEK | Smartpack2 Basic Industrial Controller (Replacement for 242100.601, 242100.601.IN, or 242100.601.VC) Used as a replacement/spare unit for IBB, Mod HE, Ecotower, ET380, and Scalable systems Unconfigured controller that must be programmed after installation with saved profile (XML) CAN Power Requirements: 500mA supply For pre-configured controllers, use part number found in individual system tabs |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1.106 | B04 | ELTEK | DISTRIBUTION PANEL, SINGLE BUS FOR STANDALONE APPLICATIONS OR ADD TO EXISTING UNITY PLANT 19" WIDE MOUNTING 4RU REAR WIRE, INPUT, FRONT WIRE OUTPUT, 15" DEEP, MID MOUNT INPUT VOLTAGE: +/- 12/24/48VDC 600AMP BUS RATING QTY 4 INPUT CONNECTIONS 1/4'' ON 5/8'' CENTER AND QTY 1 INPUT CONNECTION 3/8" ON 1" CENTER QTY 21 BULLET CIRCUIT BREAKER POSITIONS, 1/4''-20 STUDS WITH 5/8'' CENTERS MAX CIRCUIT BREAKER SIZE 250AMPS DRY CONTACT ALARM, (2 PIN CONNECTOR WIRESET INCLUDED) (USING CBB BREAKERS ONLY) |  | 5 | 0 | 5 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1.2 | Rectifiers
1.201 | 241115.105 | ELTEK | FLATPACK2 HE RECTIFIER 2000W 48V, -INPUT: 85-300VAC, FAN COOLED (FRONT TO BACK); -OUTPUT: 2000W @ 185-300VAC, 2000W @ 185VAC LINEARLY TO 850 W @ 85VAC. -EFFICIENCY: >96.5%; -OPERATING TEMPERATURE -40 TO +45°C: 2000W; LINEARLY DETATE FROM 2000W @ 45°C TO 1350W @ 75°C; SHUTDOWN AT 75°C, AUTOMATICALLY RESTART AT LOWER TEMPERATURE. -STORAGE TEMPERATURE: -40 TO +85°C -DIMENSION & WEIGHT: 4.29"W x 1.69"H x 13"D; 4.3 LBS |  | 48 | 0 |  | 0 | 4 | 0 | 8 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 |  | 0
1.202 | 241119.105 | ELTEK | FLATPACK2 HE RECTIFIER 3000W 48V, -INPUT: 85-305VAC; FAN COOLED (FRONT TO BACK); -OUTPUT: 3000W @ 176-305VAC, 3000W @ 176VAC LINEARLY TO 1382W @ 85VAC. -EFFICIENCY: >96.2%; -OPERATING TEMPERATURE: -40 TO +45°C: 3000W; LINEARLY DERATE FROM 3000W @ 46°C TO 2100W @ 75°C; SHUTDOWN AT 75°C, AUTOMATICALLY RESTART AT LOWER TEMPERATURE -STORAGE TEMPERATURE: -40 TO +85°C -DIMENSION & WEIGHT: 4.29"W x 1.69"H x 13"D; 4.3 LBS |  | 18 | 0 | 15 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 3 | 0
1.203 | 331E23640800 | ELTEK | BLIND PANEL FP2 HE BLACK G1 |  | 43 | 0 | 3 | 0 | 4 | 0 |  | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 |  | 0
1.3 | DC Breakers
1.301 | CBB250M | ELTEK | CIRCUIT BREAKER, 250 AMP TRIPLE POLE PLUG-IN BULLET, MID-TRIP INCLUDES 3798102673 TRIPLE POLE STRAP 3/8" X 1" CENTER |  | 32 | 0 | 5 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 5 | 0
1.302 | USKIT-00023 | ELTEK | 800A Battery Disconnect Panel Kit 19 or 23" 19" wide, included extender brackets to 23" 4 RU high panel 800A circuit breaker disconnect Qty 2 dual hole 3/8-1" input for power system connection, max 350mcm cable Qty 3 dual hole 3/8-1" output for battery connection, max 350mcm cable or Qty 2 777mcm cable Form C alarm contact for breaker alarm (C and NC), alarm cable included Alarm jumper cable included to go panel to panel. |  | 2 | 0 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1.4 | AC Breakers
1.401 | GHB3030, BAB3030 | PLATT (BREMERTON | 40A, 3 Pole Breaker for Eaton PRL1A Panels |  | 6 | 0 | 5 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 1 | 0
2 | Racks & Accessories
2.1 | Racks
2.101 | 3900106800 | ELTEK | SEISMIC RELAY RACK 23" INCHES WIDE 7' FEET HIGH WITH A 5" RAIL WIDTH WELDED RACK WITH APPROXIMATE WEIGHT OF 100 POUNDS EMPTY 44 USABLE RACK SPACES |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2.102 | Various | Various | Installation Kit, (Includes Concrete Floor Anchors, Overhead Bracing) |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2.2 | Control and Alarm Cables
2.201 | CA210203104 | ELTEK | ALARM CABLE CONNECTS CONTROLLER ALARM RELAYS TO CUSTOMER’S ALARM TRANSPORT EQUIPMENT - 10' LENGTH - 20-PIN CONNECTOR ON CONTROLLER END - DISCRETE SOLID CORE, 24 AWG WIRE ON CUSTOMER END |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2.202 | 3672495500 | ELTEK | ALARM CABLE CONNECTS CONTROLLER ALARM RELAYS TO CUSTOMER’S ALARM TRANSPORT EQUIPMENT - 50' LENGTH - 20-PIN CONNECTOR ON CONTROLLER END - DISCRETE SOLID CORE, 24 AWG WIRE ON CUSTOMER END |  | 10 | 0 |  | 0 | 1 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
2.003 | CA210203106 | ELTEK | ALARM CABLE CONNECTS CONTROLLER ALARM RELAYS TO CUSTOMER’S ALARM TRANSPORT EQUIPMENT - 100' LENGTH - 20-PIN CONNECTOR ON CONTROLLER END - DISCRETE SOLID CORE, 24 AWG WIRE ON CUSTOMER END |  | 2 | 0 | 1 | 0 |  | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
3 | Battery Systems
3.001 | DDmP125-27 |  | Enersys Battery System, 1 String, 24 Cells, 4 Wide (Gold Mtn replacement, 2 strings required) |  | 2 | 0 |  | 0 |  | 0 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
3.002 | DDmP125-33 |  | Enersys Battery System, 1 String, 24 Cells, 4 Wide (Cencom, new, 2 strings required) |  | 2 | 0 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4 | Power Cables
4.1 | Battery Cables
4.101 | Southwire #57149801 | Graybar | TelcoFlex L2 Central Office Cable, 500MCM, COPPER, STRANDED, TRAY RATED, COLOR BLACK, 90 degrees C - Parallel Battery Cables for Modular HE Rectifiers, LOOP LENGTH < 80 FT. |  | 400 | 0 | 400 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4.102 | Various (Panduit, Ilsco, Burndy) | Various | Two Hole, Compression Lugs, 500MCM, Long Barrel, Inspection Window, 3/8" Hole, 1" Spacing |  | 10 | 0 | 10 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4.103 | N/A | N/A | Battery Cables for Replacement Unity Rectifiers (re-use existing 1/0 AWG, AWM battery cables) |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4.104 | N/A | N/A | Lugs for Unity Battery Cables, 1/0 AWG (not required, re-use existing battery cables) |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4.105 | DOX8 | SitePro1 | Anti Oxidant Joint Compound, 8oz. |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4.106 | GHK38 | Sitepro1 | Stainless Steel Hardware Kit (3/8" x 1-1/4" 10 pk) includes hex bolt, flat washer, split washer , and nut |  | 13 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
4.2 | Load Cables
4.201 | Southwire #57128501 | Graybar | TelcoFlex L2 Central Office Cable, AWG 4/0, Copper, Tray-rated, Black, 90 degrees C for Load Distribution Cables - Modular HE to Aux. Dist. |  | 700 | 0 | 700 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4.202 | Various (Panduit, Ilsco, Burndy) | Various | Two Hole, Compression Lugs, AWG 4/0, Long Barrel, Inspection Window, 3/8" Hole, 1" Spacing for Load Distribution Cables at Cencom |  | 25 | 0 | 25 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4.203 | Southwire #56977001 | Graybar | TelcoFlex L2 Central Office Cable, AWG 2/0, Copper, Tray-rated, Black, 90 degrees C for Load Distribution Cables - Unity to existing dist. |  | 330 | 0 |  | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 | 30 | 0 |  | 0
4.204 | Various (Panduit, Ilsco, Burndy) | Various | Two Hole, Compression Lugs, AWG 2/0, Long Barrel, Inspection Window, 3/8" Hole, 1" Spacing for Load Distribution Cables |  | 55 | 0 |  | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 |  | 0
5 | Professional Services
5.1 | Engineering Services
5.101 | (Provide if proposed) |  | (Provide Detailed Description) |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.102 | (Provide if proposed) |  | (Provide Detailed Description) |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.2 | Field Services
5.201 | Unity Rectifier Replacement |  | Replace Unity Rectifier Systems ( Single battery systems) |  | 10 | 0 |  | 0 | 1 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.202 | Unity Rectifier Replacement |  | Replace Unity Rectifier Systems (Dual battery systems) |  | 1 | 0 |  | 0 |  | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.203 | Modular Recitifier Installation |  | Install New Modular Rectifier System |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.204 | Battery Replacement |  | Replace Existing Batteries at Gold Mountain |  | 1 | 0 |  | 0 |  | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.205 | Battery Installation |  | Install New Batteries at Cencom |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.3 | Equipment Removal and Disposal
5.301 | Old Flatpack Rectifier |  | Remove and Dispose of Old Eltek Flatpack Rectifiers |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.302 | Batteries |  | Remove Dispose of Gold Mountain Batteries |  | 1 | 0 |  | 0 |  | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.303 | Batteries |  | Remove an Dispose of Cencom Batteries |  | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.304 | Batteries |  | Lead Credit (lbs.) |  | 10400 | 0 | 2400 | 0 |  | 0 | 8000 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.4 | Other
5.401 | Operation and Maintenance Services |  | Modular Rectifer Operations and Maintenance Costs - Year 1 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.402 | Operation and Maintenance Services |  | Modular Rectifer Operations and Maintenance Costs - Year 2 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.403 | Operation and Maintenance Services |  | Modular Rectifer Operations and Maintenance Costs - Year 3 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.404 | Operation and Maintenance Services |  | Modular Rectifer Operations and Maintenance Costs - Year 4 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.405 | Operation and Maintenance Services |  | Modular Rectifer Operations and Maintenance Costs - Year 5 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.406 | Operation and Maintenance Services |  | Modular Rectifer Operations and Maintenance Costs - Year 6 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.407 | Operation and Maintenance Services |  | Modular Rectifer Operations and Maintenance Costs - Year 7 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5.408 | Operation and Maintenance Services |  | Unity Rectifier Operations and Maintenance Costs - Year 1 | 0 | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.409 | Operation and Maintenance Services |  | Unity Rectifier Operations and Maintenance Costs - Year 2 | 0 | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.41 | Operation and Maintenance Services |  | Unity Rectifier Operations and Maintenance Costs - Year 3 | 0 | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.411 | Operation and Maintenance Services |  | Unity Rectifier Operations and Maintenance Costs - Year 4 | 0 | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.412 | Operation and Maintenance Services |  | Unity Rectifier Operations and Maintenance Costs - Year 5 | 0 | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.413 | Operation and Maintenance Services |  | Unity Rectifier Operations and Maintenance Costs - Year 6 | 0 | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.414 | Operation and Maintenance Services |  | Unity Rectifier Operations and Maintenance Costs - Year 7 | 0 | 11 | 0 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.415 | Operation and Maintenance Services |  | Battery Operations and Maintenance Costs - Year 1 | 0 | 12 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.416 | Operation and Maintenance Services |  | Battery Operations and Maintenance Costs - Year 2 | 0 | 12 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.417 | Operation and Maintenance Services |  | Battery Operations and Maintenance Costs - Year 3 | 0 | 12 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.418 | Operation and Maintenance Services |  | Battery Operations and Maintenance Costs - Year 4 | 0 | 12 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.419 | Operation and Maintenance Services |  | Battery Operations and Maintenance Costs - Year 5 | 0 | 12 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.42 | Operation and Maintenance Services |  | Battery Operations and Maintenance Costs - Year 6 | 0 | 12 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.421 | Operation and Maintenance Services |  | Battery Operations and Maintenance Costs - Year 7 | 0 | 12 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |  | 0
5.422 | Training |  | Training | 0 | 2 | 0 | 1 | 0 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6 | Freight & Other
6.1 | Freight WA |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6.2 | Applicable Taxes |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6.3 | Management Discounts |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6.4 | Other |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Grand Total |  | Less any Applicable Taxes |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## New Site BOM&S
NS
| PRODUCT CODE |  | EQUIPMENT LIST | UNIT | SYSTEM |  | NEW SITE
ITEM | PART NUMBER | SUPPLIER | DESCRIPTION | PRICE | QTY | PRICE | QTY | PRICE
1 | RECTIFIER SYSTEMS
1.1 | Rectifer System
1.101 | UNT20806.00012 | ELTEK | UNITY POWER SYSTEM WITH FLATPACK2 - 48V, 500A POWER SHELF - RECTIFIER POSITIONS: QTY 8 (SUPPORTS BOTH 2000W and 3000W RECTIFIERS) - INPUT CONNECTIONS: REAR ACCESS TO TERMINAL BLOCK, ONE INPUT PER RECTIFIER, DUAL FEED JUMPERS INCLUDED PRIMARY DISTRIBUTION: 23" WIDE, NEGATIVE VOLTAGE OUTPUT QTY 26 CIRCUIT BREAKER POSITIONS (CBB STYLE) 1/4"-20 STUD 5/8" CENTER -QTY 26 LOAD BREAKER POSITIONS QTY 3 BULK LOAD POSITIONS -QTY 1: 3/8"-16 NUTS ON 1" CENTER -QTY 2: 1/4"-20 NUTS ON 5/8" CENTER BULK BATTERY POSITIONS THRU A SHUNT & LVBD -QTY 7: 3/8"-16 STUDS ON 1" CENTER OR QTY 8: 1/4"-20 NUTS ON 5/8" CENTER SMARTPACK S PANEL MOUNT CONTROLLER INCLUDED SPSP-UNT600-A01 UNT-F4808I-C14N |  | 1 | 0 | 1 | 0
1.102 | D07 | ELTEK | DISTRIBUTION PANEL, SINGLE BUS FOR STANDALONE APPLICATIONS OR ADD TO EXISTING UNITY PLANT 23" WIDE MOUNTING 4RU REAR WIRE INPUT, FRONT WIRE OUPUT, 15" DEEP, MID MOUNT INPUT VOLTAGE: +/- 12/24/48VDC 600AMP BUS RATING QTY 4 INPUT CONNECTIONS 1/4'' ON 5/8'' CENTER AND QTY 1 INPUT CONNECTION 3/8" ON 1" CENTER QTY 26 BULLET CIRCUIT BREAKER POSITIONS, 1/4''-20 STUDS WITH 5/8'' CENTERS MAX CIRCUIT BREAKER SIZE 250AMPS DRY CONTACT ALARM, (2 PIN CONNECTOR WIRESET INCLUDED) (USING CBB BREAKERS ONLY) |  | 1 | 0 | 1 | 0
1.2 | Rectifiers
1.201 | 241115.105 | ELTEK | FLATPACK2 HE RECTIFIER 2000W 48V, -INPUT: 85-300VAC, FAN COOLED (FRONT TO BACK); -OUTPUT: 2000W @ 185-300VAC, 2000W @ 185VAC LINEARLY TO 850 W @ 85VAC. -EFFICIENCY: >96.5%; -OPERATING TEMPERATURE -40 TO +45°C: 2000W; LINEARLY DETATE FROM 2000W @ 45°C TO 1350W @ 75°C; SHUTDOWN AT 75°C, AUTOMATICALLY RESTART AT LOWER TEMPERATURE. -STORAGE TEMPERATURE: -40 TO +85°C -DIMENSION & WEIGHT: 4.29"W x 1.69"H x 13"D; 4.3 LBS |  | 4 | 0 | 4 | 0
1.203 | 331E23640800 | ELTEK | BLIND PANEL FP2 HE BLACK G1 |  | 4 | 0 | 4 | 0
1.3 | DC Breakers
1.301 | VH224N | CED (BREMERTON) | Square D 200A Fused Safety Switch (Battery Disconnect Switch) |  | 1 | 0 | 1 | 0
1.302 | FRNR200 | CED (BREMERTON) | Bussman 200A Fuse Class R (10,000 AIC) |  | 2 | 0 | 2 | 0
1.4 | AC Breakers
1.401 | Various | Various | 30A, 2 Pole Breaker (Provided by Others) | 0 | 0 | 0 | 0 | 0
2 | Racks & Accessories
2.1 | Racks
2.101 | 3900106800 | ELTEK | SEISMIC RELAY RACK 23" INCHES WIDE 7' FEET HIGH WITH A 5" RAIL WIDTH WELDED RACK WITH APPROXIMATE WEIGHT OF 100 POUNDS EMPTY 44 USABLE RACK SPACES |  | 1 | 0 | 1 | 0
2.102 | Various | Various | Installation Kit, (Includes Concrete Floor Anchors, Overhead Bracing) |  | 1 | 0 | 1 | 0
2.2 | Control and Alarm Cables
2.201 | CA210203104 | ELTEK | ALARM CABLE CONNECTS CONTROLLER ALARM RELAYS TO CUSTOMER’S ALARM TRANSPORT EQUIPMENT - 10' LENGTH - 20-PIN CONNECTOR ON CONTROLLER END - DISCRETE SOLID CORE, 24 AWG WIRE ON CUSTOMER END |  | 0 | 0 |  | 0
2.202 | 3672495500 | ELTEK | ALARM CABLE CONNECTS CONTROLLER ALARM RELAYS TO CUSTOMER’S ALARM TRANSPORT EQUIPMENT - 50' LENGTH - 20-PIN CONNECTOR ON CONTROLLER END - DISCRETE SOLID CORE, 24 AWG WIRE ON CUSTOMER END |  | 1 | 0 | 1 | 0
2.003 | CA210203106 | ELTEK | ALARM CABLE CONNECTS CONTROLLER ALARM RELAYS TO CUSTOMER’S ALARM TRANSPORT EQUIPMENT - 100' LENGTH - 20-PIN CONNECTOR ON CONTROLLER END - DISCRETE SOLID CORE, 24 AWG WIRE ON CUSTOMER END |  | 0 | 0 | 0 | 0
3 | Battery Systems
3.001 | DDmP85-13 |  | Enersys Battery System, 1 String, 24 Cells, 4 Wide |  | 1 | 0 | 1 | 0
4 | Power Cables
4.1 | Battery Cables
4.101 | Southwire #57128501 | Graybar | TelcoFlex L2 Central Office Cable, AWG 4/0, Copper, Tray-rated, Black, 90 degrees C - Battery Cables for Unity Rectifier, loop length <50 Ft. |  | 50 | 0 | 50 | 0
4.102 | Various (Panduit, Ilsco, Burndy) | Various | Two Hole, Compression Lugs, AWG 4/0, Long Barrel, Inspection Window, 3/8" Hole, 1" Spacing for Load Distribution Cables at Cencom |  | 4 | 0 | 4 | 0
4.103 | DOX8 | SitePro1 | Anti Oxidant Joint Compound, 8oz. |  | 1 | 0 | 1 | 0
4.104 | GHK38 | Sitepro1 | Stainless Steel Hardware Kit (3/8" x 1-1/4" 10 pk) includes hex bolt, flat washer, split washer , and nut |  | 2 | 0 | 2 | 0
4.2 | Load Cables
4.201 | Southwire #56977001 | Graybar | TelcoFlex L2 Central Office Cable, AWG 2/0, Copper, Tray-rated, Black, 90 degrees C for Load Distribution Cables - Unity to existing dist. |  | 20 | 0 | 20 | 0
4.202 | Various (Panduit, Ilsco, Burndy) | Various | Two Hole, Compression Lugs, AWG 2/0, Long Barrel, Inspection Window, 3/8" Hole, 1" Spacing for Load Distribution Cables |  | 4 | 0 | 4 | 0
5 | Professional Services
5.1 | Engineering Services
5.101 | (Provide if proposed) |  | (Provide Detailed Description) | 0 | 0 | 0 |  | 0
5.102 | (Provide if proposed) |  | (Provide Detailed Description) | 0 | 0 | 0 |  | 0
5.2 | Field Services
5.201 | Unity Rectifier Installation |  | Install Unity Rectifier System | 0 | 1 | 0 | 1 | 0
5.205 | Battery Installation |  | Install New Batteries | 0 | 1 | 0 | 1 | 0
5.3 | Equipment Removal and Disposal
5.301 | N/A |  | N/A
5.4 | Other
5.401 | Operation and Maintenance Services |  | Operations and Maintenance Costs - Year 1 | 0 | 1 | 0 | 1 | 0
5.402 | Operation and Maintenance Services |  | Operations and Maintenance Costs - Year 2 | 0 | 1 | 0 | 1 | 0
5.403 | Operation and Maintenance Services |  | Operations and Maintenance Costs - Year 3 | 0 | 1 | 0 | 1 | 0
5.404 | Operation and Maintenance Services |  | Operations and Maintenance Costs - Year 4 | 0 | 1 | 0 | 1 | 0
5.405 | Operation and Maintenance Services |  | Operations and Maintenance Costs - Year 5 | 0 | 1 | 0 | 1 | 0
5.406 | Operation and Maintenance Services |  | Operations and Maintenance Costs - Year 6 | 0 | 1 | 0 | 1 | 0
5.407 | Operation and Maintenance Services |  | Operations and Maintenance Costs - Year 7 | 0 | 1 | 0 | 1 | 0
6 | Freight & Other
6.1 | Freight WA |  |  | 0 | 1 | 0 | 1 | 0
6.2 | Applicable Taxes |  |  | 0 | 1 | 0 | 1 | 0
6.3 | Management Discounts |  |  | 0 | 1 | 0 | 1 | 0
6.4 | Other |  |  | 0 |  | 0 | 1 | 0
| Grand Total |  | Less any Applicable Taxes |  |  | 0 |  | 0